## CS PWG 004-1 INSTR
CALCULATION SHEET |  | CS PWG 004 INSTR.
PWG Filtration system - SA unit size Instructions |  | date | 2017-05-08
|  | revision | 1
|  | page | 1 / 2
Dirck Demeyer, R&D Engineer
translation :
Use of the Calculation Sheet for SA units sizes
→ | The set-up is to fill in a number of required data, like water quality and user information.
→ | Filter sand is often applied as a pre-treatment; a confirmation of the nature of filtration, that only
sediment particles need to be removed with a given minimum particle cut-off for SA and SAHA
is required. If the water quality shows differently, a second confirmation is required to continue.
→ | The grade of water clearness, based on NTU value or cm transparency, is used to determine
the size of the SA unit.
→ | The limit values for each cell to be filled in are shown in the cell comments ( red triangle ).
→ | Error messages disappear the moment the values in a group of cells is filled in correctly.
→ | If certain user data not match, it may be necessary to adapt the data.
→ | The overview of the complete range under given conditions is guiding for these adaptions.
Instructions
1. | Make a copy and save it under the client/case name in your personal files.
Make sure that in this copy all selectable cells are cleared and the adaption factors are set on 1.
The nature of filtration is pre-set and so not selectable.
2. | Fill in the Request data ; this allows to identify the sheet in relationship to the specific data.
It is recommended to start up the Axapta offer, so the OF number could here be filled in.
3. | Select SA for Filter sand or SAHA for Filter sand with extra Hydro Anthracite.
SAHA gives no other improvement to SA than a slightly lower particle size cut-off.
The error "particle size cut-off" disappears.
3. | Fill in Water Quality with the corresponding units.
NTU or ppm SS are only indicative and filled in when available; an estimation for NTU is made
according ppm SS.
Data on pH, biological contamination, Fe or MN presence and colour is obliged and the error
" water quality" disappears after correct fill-in.
4. | In case the water quality is unacceptable or data are filled in incompletely, an additional treatment
is popped up. To continue the calculation, the error must be accepted by confirmation with yes
in the this line. The error "water quality" turns into green and further progress of the CS is allowed.
5. | Turbidity measurements are not always done or are often influenced by water colour. Therefor,
the calculation sheet is using the personal perception of grades of clearness. The calculator
fills in yes next to the chosen grade, based on the available data;
the client agrees with the calculation.
6. | Grade 1 and grade 7 are indicating the out of scope for the Filter sand and corresponding
additional treatments are popped up. The calculation can not be continued.
In the other cases, the grade 1-7 error disappears.
7. | Fill in the User Information. The "3 user data" error disappears.
8. | In case the sand filter is rinsed with clean water, fill in yes. The CS will give the minimum
required clean water storage for a single filter and double as much for 2 rinses in sequence.
Otherwise, fill in no. "Clean rinse water" error disappears.
9. | The CS shows now the recommended linear velocity according the set water clearness.
In case the filled in user data match with one single unit size or 2 parallel units sizes, this
size will be shown in green, together with the maximum allowed service flow rate, effective
linear velocity @ given service flow rate and estimated days between rinse.
CALCULATION SHEET |  | CS PWG 004 INSTR.
PWG Filtration system - SA unit size Instructions |  | date | 2017-05-08
|  | revision | 1
|  | page | 2 / 2
Dirck Demeyer, R&D Engineer
translation : | 0
10. | If no size is shown, the user data can be adapted according the shown data for the complete
range. Look for the unit size which may give the required flow rate and fill in the mentioned
minimum rinse flow rate in the cell of pump flow rate.
11. | Only the smallest possible unit size is shown. If due to high daily water consumption and/or
high particle charge, the days capacity becomes < 1 day, the unit size must be chosen larger.
A supplementary green table will show the g capacity / day according user data. Look for the
value of g capacity in the range overview of the unit size which is indicated as green and fill
this in as g smallest size. Look then for the unit size which has sufficient g capacity to run
for at least 1 day and fill this value in as g required size. The CS will show the minimum
adaption factor to lower down the linear velocity. Fill this or similar values in below the velocity
in order to adjust the settings, until at least 1 day capacity is reached.
Under these conditions of high daily charge, the filter bed will have the minimum 1 day capacity
but will filter at lower linear velocity than theoretically required.
Be aware that also corresponding adjustment must be done for the pump flow rate !
Note : the CS will check again the match of all 3 user data, which may not have increased equally;
small decimal adaptions could finally result in a perfect match.
12. | Do a similar adaption for the 2 parallel units calculation result.
Due to the necessary adaptions of the user data to get a match for the single unit size or for
the 2 parallel units size, it will not be possible to have a result for both options ( single/parallel)
if is chosen for the smallest increase of the required pump capacity. The parallel option is so
recommended.
In case of a specific request of the customer for or single or parallel, or in case the calculator
wishes to make only one clear proposal, it is possible to cancel 1 of the 2 optional proposals
by fill in the adaption factor for that option as 0.
13. | Important note : the CS is trying to find the best solution according filled in data. To find the
required size increase to reach the desired g capacity, make sure that the adaption factor is
reset to 1 in order to consult the range overview.
14. | As a result of the size adaption, if this is the case, the minimum required clean rinse water
storage will accordingly be increased and will pop up in the User information frame, only when
rinse with clean water was filled in as yes.
15. | In case clean water rinse is filled in as no and a 2 parallel units size is proposed with a pump
capacity which is insufficient to feed 1 rinse + required service flow, a supplementary error
will pop up with the required minimum pump flow rate to adapt the user data.